GUIDE SPECIFICATIONS

Wiremold®  V500 Series Raceway

V500 One-piece metal raceway

PART 1 GENERAL

1.1	Scope

This specification covers a surface metal raceway system used for branch circuit wiring or data network, voice, video and other low-voltage wiring. The metal raceway system shall consist of raceway, appropriate fittings and device boxes to complete installation per electrical drawings.

1.2	Classification and Use

Surface metal raceway is to be utilized in dry interior locations only as covered in Article 386 of the National Electrical Code, as adopted by the National Fire Protection Association and as approved by the American National Standards Institute. The Wiremold Company’s V500 Raceway System is listed by Underwriters Laboratories under File Nos. E4376 Guide RJBT and E41751 Guide RJPR.

PART 2 PRODUCT

2.1	Manufacturer

The surface metal raceway system specified herein for branch circuit wiring or data network, voice, video and other low-voltage wiring shall be the V500 System as manufactured by The Wiremold Company. Systems of other manufacturers may be considered equal if, in the opinion, and the written approval of the engineer, they meet all the performance standards specified herein.

2.2	Materials

The raceway and all system components must be UL Listed. They shall be manufactured of steel; zinc plated, galvanized and/or finished in ivory ScuffCoat™ (a polyester topcoat over ivory base) and shall be suitable for field repainting to match surroundings.

2.2.1 Raceway

The raceway shall be a one-piece design with a base and cover factory assembled. Total width shall be 0.75" by 0.53" [19.05mm by 13.46mm] deep with a cross sectional area of 0.20 square inches [129mm2]. The raceway base and cover shall have an approximate thickness of .040" [10.16mm]. The raceway shall be available in 5' and 10' [1.52m and 3.048m] lengths.

A hand operated cutting tool shall be available for the base and cover to ensure clean,

square cuts.

2.2.2 Fittings

A full compliment of fittings must be available including but not limited to mounting clips and straps, couplings, flat, internal and external elbows, cover clips, tees, entrance fittings, conduit connectors 
and bushings. The covers shall be painted with an enamel finish, ivory in color to match the V500 Raceway. They shall overlap the raceway to hide uneven cuts. All fittings shall be supplied with a 
base where applicable. A transition fitting shall be available to adapt to other raceways manufactured 
by The Wiremold Company.

2.2.3 Device and Fixture Boxes

Device boxes shall be available for mounting standard devices and faceplates. A device box shall be available in single- and multiple-gang configurations, up to six-gang. Single-gang boxes shall allow for snap-on and fastener application. They shall range in depth from 0.94" to 2.75" [23.88mm to 69.85mm]. Extension boxes shall be available to adapt to existing standard flush switch and receptacle boxes. Round fixture and extension boxes shall be available to mount fixtures and other devices with mounting centers of 1 15/32", 1 5/8", 1 23/32", 1 27/32", 2 3/4", 3 1/2" and 4 1/16" [37.29mm, 41.27mm, 43.65mm, 46.83mm, 69.85mm, 88.90mm, and 103.12mm] diameters. Round fixture and extension boxes shall be available in depths ranging from 0.47" to 1.00" [11.94mm to 25.4mm] and in diameters of 3.00", 4.75", 5.50" and 6.38" [76.2, 120.65, 139.7, and 162.05]. All device and fixture box covers shall be painted with an enamel finish, ivory in color to match the raceway cover.

2.2.4 Communication Devices and Accessories

The raceway manufacturer will provide a complete line of connectivity outlets and modular inserts for UTP/STP, Fiber Optic, Coaxial and other cabling types with face plates and bezels to facilitate mounting. A complete line of preprinted station and port identification labels, snap-in icon buttons as well as write-on station identification labels shall be available.

PART 3 EXECUTION

3.1 	Installation

Prior to and during installation, refer to system layout drawing containing all elements of the system. Installer shall comply with detailed manufacturer’s instruction sheets, which accompany system components as well as complete system instruction sheets - whichever 
is applicable.

3.1.1 Mechanical Security

All raceway systems shall be mechanically continuous and connected to all electrical outlets, boxes, and cabinets, in accordance with manufacturer’s installation sheets.

3.1.2 Electrical Security

All metal raceway shall be electrically continuous and bonded in accordance with the National Electric Code for proper grounding.

3.1.3 Raceway Support

Raceway shall be securely supported at intervals not exceeding 10' [3.048m] or in accordance with manufacturer’s installation sheets.

3.1.4 Completeness

All raceway systems shall be installed complete, including insulating bushings and inserts where required by manufacturer’s installation sheets. All unused raceway openings shall be closed.

|  | Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2005 Legrand All Rights Reserved | ED498R3 – Updated January 2005 – For latest specs visit www.legrand.us |