www.wattstopper.com

800.879.8585

# Text boxes

## SPECIFICATIONS

CX-100

CX-105

- The passive infrared sensor shall be capable of detecting presence in the control area by detecting changes in the infrared energy. Small movements shall be detected such as when a person is writing while seated at a desk within 15 feet of the sensor.

- To avoid false ON activations and to provide high sensitivity to minor motion, Pulse Count Processing and Detection Signature Analysis shall be used to examine the frequency, duration, and amplitude of the signal received by the sensor to respond only to those signals caused by human motion.

- Sensor shall utilize mixed signal ASIC (application-specific integrated circuit) technology, which combines analog and digital processing into one chip package, to provide immunity to RFI and EMI.

- Sensor shall utilize a temperature compensated dual element sensor and a multi-element Fresnel lens.

- Fresnel lens shall be a Poly IR 4 based material (for standard and Long Range lens) to offer superior filtering capability of competing light sources, such as the sun and other visible light sources. The lens shall have grooves facing in to avoid dust and residue build up which affects IR reception. Aisleway lenses shall be a Poly IR 2 based material that offers greater sensitivity to motion and superior detection performance.

- To ensure sensitivity to small motion at the desk top, the sensor shall have a standard 30 element lens with 15 layers horizontally and 4 layers vertically; a 14 element Long Range lens with 9 layers horizontally and 4 layers vertically; a 9 element 1-sided Aisle Way lens with 9 layers vertically; or an 18 element 2-sided Aisle Way lens with 9 layers vertically.

- Sensor shall cover up to 2000 square feet with the Standard Lens, up to 90 linear feet with the Long Range Lens, up to 120 linear feet with the 2-Sided Aisle Way Lens, and up to 50 linear feet with the 1-Sided Aisle Way lens for walking motion when mounted at a ceiling height of 10 feet

- The CX-100 shall have an additional single pole, double throw isolated relay with normally open, normally closed, and common outputs rated for 1 Amp at 24 VDC. The isolated relay is for use with HVAC control, data logging, and other control options.

- The CX-100 shall have two outputs; one output is based on occupancy only and one is based on occupancy with a hold OFF and an internal photocell setting when a minimum light level is present (adjustable from 3 to 200 footcandles). CX-105 shall have only an occupancy based output.

- For accuracy and consistency, sensor shall have a DIP switch controlled, digital time delay adjustable from 15 seconds to 30 minutes.

- Sensor shall have user-adjustable sensitivity settings.

- Sensor shall be furnished with a DIP switch override-ON function for use in the event of failure.

- Adjustments and mounting hardware shall be concealed under a removable cover to prevent tampering of adjustments and hardware.

- Sensor can be wired in parallel to allow coverage of large areas.

- To ensure quality and reliability, sensor shall be manufactured by an ISO 9002 certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Sensor shall have standard 5 year warranty.

- Sensor shall be UL and CUL listed.

### CX Passive Infrared Occupancy Sensor

www.wattstopper.com

800.879.8585

CX1001204