www.wattstopper.com

800.879.8585

# Text boxes

## SPECIFICATIONS

EW-200

EW-100

EWF-205

EWF-105

EW-205-24

EW-105-24

- Sensor shall be a completely self-contained device capable of detecting presence in the controlled range by detecting changes between infrared energy in motion and the background space.

- To increase detection density and accuracy of motion detection, sensor shall employ dual PIR detectors and a three level Fresnel lens.

- To avoid false ON activations and to provide high sensitivity to minor motion, Pulse Count Processing and Detection Signature Analysis shall be used to examine the frequency, duration, and amplitude of the signal received by the sensor to ensure response only to those signals caused by human motion.

- To enhance relay life and reduce circuitry noise, line voltage EW sensors shall use Zero Crossing circuitry.

- To increase reliability, sensor shall utilize mixed signal ASIC (application-specific integrated circuit) technology that combines analog and digital processing into one microprocessor.

- To facilitate simplified installation, sensor shall be capable of mounting vertically or horizontally onto a standard outdoor junction box in a variety of locations, such as walls, ceilings, or eaves.

- EW-100 and EW-105 sensors shall cover up to 35 feet, with a field of view of 180 degrees. EW-200 and EW-205 sensors shall cover up to 52.5 feet, with a field of view of 270 degrees.

- Sensor shall have an operating temperature range of -40°F to +130°F.

- The outdoor sensor shall carry a UL rating of 773A as a raintight device.

- To ensure complete protection from weather elements and exposure, sensor shall be manufactured with precision double-shot tooling and contain internal silicon gaskets.

- Sensor shall include a built-in light level sensor, adjustable by the user, that will keep lights from turning on during daylight hours.

- Sensor shall have user-adjustable time delay settings, including an override ON option that enables controlled lights to be turned on remotely for the length of the time delay.

- The EW-100 and EW-200 sensors shall have an additional single pole, double throw isolated relay with normally open, normally closed, and common outputs rated for 1 Amp at 24 VDC. The isolated relay is for use with HVAC control, data logging, and other control options.

- The EW-105-24 and EW-205-24 sensors shall operate at 24 VDC and shall be capable of working in conjunction with The Watt Stopper’s DM-105-WP bi-level outdoor controllers for controlling HID lighting.

- EW-100, EW-200 and EWF sensors shall operate at either 120 VAC or 277 VAC, 60 Hz.

- EW-100, EW-200 and EWF sensors shall be compatible with all electronic ballasts and PL lamp ballast systems.

- EWF sensors shall utilize polycarbonate lamp holders that accept PAR 20 or 38 lamps up to 150W per lamp.

- EWF sensor lamp holders shall carry a UL rating of 1571 for wet locations.

- To ensure quality and reliability, sensor shall be manufactured by an ISO 9002 certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Sensor shall have a standard five year warranty, and be UL and CUL listed.

### EW Outdoor Motion Sensors

www.wattstopper.com

800.879.8585

EW1204