Guideform Specification

LP LIGHTING CONTROL PANEL

AIA Division 16 Specifications - Section 16950

#### OVERVIEW

Watt Stopper/Legrand designs and manufactures lighting control products and systems. Products range from basic control components through mid-range systems designed for small to medium buildings, to fully automated, networked systems featuring comprehensive control software.

The LP8 is a lighting control relay panel of up to eight relays for simple exterior and interior lighting control applications. It features an 8-channel time clock for time scheduled or astronomic lighting control. Relays are assigned to one of 8 channels for flexible control of a single or a group of relays. Connection for an exterior photocell (EM24-A2) provides integrated control of exterior lighting based on light level and time schedules. 8 universal switch inputs control relays through the use of low voltage switches, occupancy sensors, daylighting photocells or other control devices. The LP8 also provides interior lighting shutoff control when used in conjunction with AS-100 automatic control switches.

The LP24 panel incorporates a larger enclosure equipped with two sections of DIN rail mounting that accommodates up to 12 four-pole contactors. This configuration is ideal for controlling exterior lighting with multi-phase circuits. The LP24 also provides economical control for interior applications with larger loads that require eight or less channels of control. In LP24 configurations using multi-pole contactors, control of the contactor coils is provided by the single pole relays. It is also possible to mix single pole and multi-pole circuit control in the same LP24 with up to eight channels of control.

IDEAL APPLICATIONS

Small office buildings

Parking lots or garages

Small to medium retail stores

Exterior building and site lighting

School exterior lighting

Sign lighting

If you have any questions or would like technical support, please contact your local Watt Stopper representative or Watt Stopper’s system applications team at 800-852-2778.

To download the latest versions of this specification and all product cut sheets go to: http://www.wattstopper.com

## PART 1 GENERAL

1.01	INTRODUCTION

The work covered in this section is subject to all of the requirements in the General Conditions of the Specifications. Contractor shall coordinate all of the work in this section with all of the trades covered in other sections of the specification to provide a complete and operable system.

1.02  SYSTEM DESCRIPTION

Install a lighting control system consisting of relay/contactor panel(s), control switches, occupancy sensors, photocells and other controlling devices. The devices are connected by low voltage and line voltage wiring. The general operation of lighting and controlled loads shall include:

Interior lighting: Manual switch and occupancy sensor control on/off with automatic time scheduled shut off.

Scheduled on/off loads: Time on, time off by automatic time schedule with after hour override capability and shutoff.

Exterior lighting: Photocell or astronomic on/time off, time on/photocell or astronomic off.

Exterior security lighting: Photocell or astronomic on, photocell or astronomic off.

1.03 QUALITY ASSURANCE

Manufacturers: Firms regularly engaged in the manufacture of lighting control equipment and ancillary equipment, of types and capacities, whose products have been in satisfactory use in similar service for not less than 5 years.

NEC Compliance: Comply with NEC as applicable to electrical wiring work.

NEMA Compliance: Comply with applicable portions of NEMA standards pertaining to types of electrical equipment and enclosures.

#### UL Approvals: UL listed under UL 916 Energy Management Equipment.

FCC Emissions: Compliance with FCC emissions Standards specified in Part 15 Subpart J for Class A application.

1.04 SUBMITTALS

Shop Drawings: Submit dimensional drawings of all lighting control system components and accessories.

One Line Diagram: Submit a one-line diagram of the proposed system configuration if it differs from that illustrated in the riser diagram included in the contract drawings.

Typical Wiring Diagrams: Submit typical wiring diagrams for all components including, but not limited to, lighting control panels, relays, contactors, photocells, switches, occupancy sensors and daylighting controls.

1.05 MANUFACTURERS

The basis of the specified system is the LP8 or LP24 lighting control relay panel manufactured by The Watt Stopper. Any other system to be considered must submit descriptive information 10 days prior to bid. Prior approval does not guarantee final approval by the electrical engineer. The contractor shall be completely responsible for providing a system meeting this specification in its entirety. All deviations from this specification must be listed and individually signed off by the consultant.

## PART 2  PRODUCTS

2.01 RELAY PANELS

- Description

  - Lighting Control Panels shall be UL listed and consist of the following:

    - Enclosure/Tub: NEMA 1.

    - Cover: Surface or Flush as required, hinged, lockable and shall restrict access to line voltage section.

    - Interior: Barrier for separation of high voltage (class 1) and low voltage (class 2) wiring. It shall include intelligence boards, power supply and control relays. Clock display and keypad shall be mounted on interior cabinet door for easy user access and programming.

- Features

- Panel shall accept up to eight single pole relays. Relays shall be individual latching relays with 20 Amp load contacts for ballast (including HID, magnetic or electronic type ballasts), tungsten and general purpose loads. Provide isolated auxiliary contacts for pilot light switching. Relays shall use quick connectors and be individually replaceable to facilitate ease of use.

- Where indicated, panels shall provide space within the high voltage section of the enclosure to accommodate up to 12 multi-pole contactors. Two sections of DIN rail mounting shall be provided as standard. No field drilling or fabrication shall be required for mounting contactors or other accessories within the enclosure.

- The lighting control panel shall provide a stagger up delay, override push buttons, pilot light outputs, and LED status light indicators for each relay or contactor control channel.

- The clock shall have a backlight display, user keypad and shall provide 8 channels of time or astronomical control. Preprogrammed lighting control scenarios shall include: scheduled on/off, manual on/scheduled off, manual on/automatic switch sweep off, astronomic or photocell on/off and astronomic or photocell control with scheduled on/off. Time clock shall provide up to 42 holidays, automatic daylight savings adjustment, astronomic coordinates by major cities, and help screens. Program memory shall be non-volatile and clock shall retain time keeping during power outages for at least 48 hours.

- The panel shall have 8 universal switch inputs that are low voltage, self-configuring and shall not require programming to accept momentary on/ momentary off switch, push button switch (cycling), maintained switch or 24VDC signals from occupancy sensors, photocells or other interfacing devices.

- Occupancy sensor and time control shall be integrated to allow occupancy sensor control after hours with hold on of lighting during occupancy scheduled time. During occupied time, control scenarios shall be selectable for time schedule of lighting on or occupancy sensor detection of lighting on initially and then hold on of lighting during occupied hours. Control shall provide selectable occupancy sensor blink warning prior to shut off and adjustable occupancy sensor time delay from the time clock keypad.

- After-hour interior lighting shut off control shall provide a full duration override time of 1 to 240 minutes with a warning blink five minutes prior to shutting the lighting off. An impending shut off will be cancelled and the override period re-initialized through the operation of any assigned switch input.

- After-hour interior lighting shut off control may be by line voltage power interrupt control to automatic control switches. The lighting control relay panel shall provide a warning blink signal to automatic control switches, thus allowing a five-minute delay prior to shutting off lighting.  The lighting shut off event may be cancelled by pressing the automatic control switch push button.  The lighting control panel time clock shall provide periodic lighting sweep signals to shut off automatic control switches.

2.02 APPROVED MANUFACTURERS

- Watt Stopper/Legrand or approved equal.

  - The contractor shall be completely responsible for providing a system that meets this specification in its entirety. All deviations from this specification must be listed and individually signed off by the consultant.

- Watt Stopper/Legrand catalog numbers.

  - Lighting control relay panel:  LP8 or LP24

  - Low voltage exterior photocell: EM24-A2

  - Automatic Control Switch: AS-100

## PART 3 EXECUTION AND SUPPORT SERVICES

3.01 INSTALLATION

All lighting control panels, switches, occupancy sensors, photocells, etc., shall be mounted as indicated on the Reflected Ceiling Plans. All wiring shall be labeled clearly indicating which lighting control panel or device it connects to. Use only properly color-coded, stranded wire as indicated on the drawings. All relays, contactors, and switches shall be tested after installation to confirm proper operation, and all connected loads shall be recorded on the lighting control schedule for each panel.

The lighting control panels shall be mounted in electrical closets or other locations as indicated on the drawings. The relay panel shall be wired to control the power of each load as indicated on the Lighting Control Panel Schedules. All power wiring will be identified with the circuit breaker number controlling the load.

3.02 CONTRACTOR PROVIDED INFORMATION

- Contractor shall provide system documentation after the equipment has been installed:

  - Lighting control operational summary sheet.

  - Programming record sheet.

  - System Installation and Operation Manual shall be provided to the owner.

3.03 WARRANTY

Manufacturer shall provide a one year warranty for all system components.

LPSPEC1204