www.wattstopper.com

800.879.8585

# Text boxes

## SPECIFICATIONS

WT-605

WT-600

WT-1105

WT-1100

WT-2205

WT-2200

WT-2255

WT-2250

- The ultrasonic occupancy sensors shall be capable of detecting presence in the floor area to be controlled by detecting doppler shifts in transmitted ultrasound.

- Ultrasonic sensing shall be volumetric in coverage with a frequency of 32.768 kHz at ±0.002%. They shall utilize Advanced Signal Processing which automatically adjusts the detection threshold dynamically to compensate for constantly changing levels of activity and air flow throughout controlled areas.

- Sensors of varying frequencies shall not be allowed so as to prevent sensors from interfering with each other and to assure compatibility in the event more sensors are added.

- Sensors shall have temperature and humidity resistant, 32 kHz tuned ultrasonic receivers. Receivers shall have less than a 6dB shift in the humidity range of 10% to 90% and less than a 10dB shift in the temperature range of -20° to 60° C.

- Detection shall be maintained when a person of average size and weight moves only within or a maximum distance of twelve inches either in a horizontal or vertical manner at the approximate speed of 12 inches per second. The sum of this distance, volume and speed represent the average condition ultrasonic sensors must meet in order for the lights to not go off when a person is reading or writing while seated at a desk.

- Sensors shall have a DIP switch override-ON function for use in the event of failure. The LED is maintained ON so as to be visible from the floor as a constant reminder that the automatic function has been by-passed.

- Sensors shall incorporate an output disable feature for easy troubleshooting.

- Sensors shall be ceiling mounted and shall not protrude more than 1.50 inches to blend in aesthetically with the ceiling. The sensors shall offer two mounting options.

- The WT-600, WT-1100, WT-2200, and WT-2250 shall have an additional single-pole, double-throw isolated relay with normally open, normally closed, and common outputs rated at 1 Amp for 24 VDC. The isolated relay is for use with HVAC control, data logging, and other control options.

- For accuracy, sensors shall have a DIP switch controlled, digital time delay that shall be adjustable from 15 seconds to 30 minutes.

- Sensors shall have user-adjustable sensitivity setting.

- Sensors shall cover 360° and up to 600 square feet for WT-605 and WT-600, 1100 square feet for WT-1005 and WT-1100, and 2200 square feet for WT-2205 and WT-2200 of walking motion.

- Hallway and corridor sensors shall be The Watt Stopper models WT-2255 and WT-2250 and shall cover up to 90 linear feet.

- Sensitivity and timer controls shall be accessible from the front of the sensor and shall be concealed by a hinged cover.

- To ensure quality and reliability, sensor shall be manufactured by an ISO 9002 certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Ultrasonic occupancy sensors shall be UL and CUL listed.

- Sensors shall have a standard 5 year warranty.

### WT Ultrasonic Occupancy Sensor

www.wattstopper.com

800.879.8585

WT1204