FS Series THRU-WALL FITTING FOR FIRE WALLS & Floors

PART 1  GENERAL

1.1	Scope

This specification covers firestop devices for use in through-penetration firestop systems, 
which are used to maintain the fire rating of the wall or floor, as well as to route and protect power and/or communications cable distribution for commercial, institutional, industrial and utility needs.

1.2	Classification and Use

The firestop device for use in through-penetration firestop systems shall have been examined and tested by Underwriters Laboratories Inc. to UL1479 (ASTM E 814) and bear the U.S. and Canadian UL Classification Mark. The device shall be classified for use in one-, two-, three-, and four-hour rated gypsum, concrete and block walls and provide a maximum L rating of 
3.3 cfm.  The device shall be classified for use in one-, two-, and three-hour rated concrete floors having a minimum 4 1/2" (114mm) thick reinforced lightweight or normal weight 
(100-150 pcf) (1600-2400 kg/m3). The devices shall also been tested by Underwriters Laboratories Inc. to UL2043 and determined to be suitable for use in air handling spaces.

PART 2  PRODUCT

2.1	Manufacturer

The firestop device specified herein shall be the FlameStopper Thru-Wall /Floor Fitting as manufactured by Wiremold/Legrand. Firestop devices of other manufacturers may be considered equal if, in the opinion and the written approval of the engineer, they meet all the performance standards specified herein.

2.2	Materials

2.2.1 Box

The firestop device box shall be constructed of 17 gauge G90 steel.

2.2.2 Intumescent Block

The firestop device intumescent block shall be constructed of a graphite base material with expansion starting at 375( F and an unrestrained expansion between 6 to 12 times. The intumescent block shall be held securely by the box in order to prevent tampering and damage during installation.

2.2.3 Adjustable Doors

The firestop device shall have doors which can be adjusted to prevent materials from penetrating the device if the device is empty or completely full. The doors shall be constructed of 16 gauge G90 steel with No. 10-32 screws use to adjust opening size.

2.2.4 Heat Shield

For retrofit applications where an existing in-wall conduit extends out from the wall more than 7/8" [22mm], the Wiremold® Heat Shield must be used in order to maintain UL Fire Classification. The firestop device is then installed onto the heat shield.

2.2.5 Split Conduit and Wall Plate

For retrofit applications where no conduit is installed in the wall to protect existing cables, the Wiremold split conduit assembly should be used to protect cables. After installing the split conduit within the wall, the Wiremold wall plate should be installed to cover any irregularly shaped hole cut in the wall. The firestop device is then installed onto the conduit.

2.3	sizes

The firestop device shall be available for 2” and 4” trade size EMT conduit.

2.4	FInish

The firestop device shall be available in red powder coat, custom colors and an unpainted galvanized finish.

PART 3  EXECUTION

3.1	Installation

Prior to and during installation, refer to the system layout or approval drawings containing all elements of the system. Installer shall comply with complete system instruction sheets.

The firestop device shall be installed in accordance with the UL Fire Resistance Directory, as well as any applicable codes and standards for general building, electrical and firestopping installation practices.

|  | Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2007 Legrand All Rights Reserved | ED1313R3 – Updated January 2007 – For latest specs visit www.legrand.us |