SECTION 26 27 26.26

ROUND FURNITURE FEED RAISED AND WOOD FLOOR BOXES

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section.

Round recessed raised and wood floor boxes.

[Insert item description.]

RELATED SECTIONS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 07 84 13.16 - Penetration Firestopping Devices.

Division 26 - Electrical:  Electrical systems and components.

Section 26 27 26.13 - Fire Classified Floor Boxes.

Division 27 - Communications:  Communications systems and components.

Division 28 - Electronic Safety and Security:  Security systems and components.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for round recessed raised and wood floor boxes.

Shop Drawings:  For the following electrical system components.  Include plans, elevations, sections, details, and attachments to other work.

Round recessed raised and wood floor boxes.

Samples:  Submit three (3) [___________] with required color and finish.  Show standard color ranges available.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of round furniture feed raised and wood floor boxes and fittings of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide fire classified floor boxes produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of round furniture feed raised and wood floor box through one (1) source from a single manufacturer.

Electrical Floor Boxes and Components:  Comply with requirements of applicable local codes, NEC, UL, and NEMA Standards pertaining to floor boxes and components.  Meet or exceed UL Fire Classification requirements for recessed and flush style boxes.  Listed and labeled in accordance with NFPA 70, Article 100.

Accessibility Compliance:  Design device flange to meet ADA Accessibility Guidelines as to changes in floor and ground surface levels.  Bevel flanges so the slope is no greater than 1:2.

DELIVERY, STORAGE AND HANDLING

Deliver floor boxes and components in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

PRODUCTS

MANUFACTURERS

Basis-of-Design Product:  The design for the round furniture feed raised and wood floor boxes are manufactured by Legrand/Wiremold, 60 Woodlawn Street, West Hartford, CT 06110; toll-free 800-621-0049, telephone 860-233-6251, fax 860-232-2062; Web Site: www.legrand.us/wiremold.

Substitutions will be considered under provisions of Section 01 25 00.

ROUND FURNITURE FEED RAISED AND WOOD FLOOR BOXES

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

Round Furniture Feed Raised and Wood Floor Boxes:  Model No. 6FF-AFB Round Furniture Feed Raised and Wood Floor Boxes manufactured by Legrand/Wiremold.

Round furniture feed raised and wood floor boxes provide an interface between power, communication and audio/video (A/V) cabling in a raised or wood floor and at the workstation or activation location where power, communication and/or A/V device services are required.  Refer to the Drawings for types.

Specifier Note:  In the following subparagraph, retain only those products that are to be incorporated into the project and delete the others.

Round furniture feed raised and wood floor boxes shall be round in shape and available in a two-gang configuration.  Boxes shall also include a removable barrier between the individual compartments for greater capacity when required.  One (1) of the two (2) compartments shall have a minimum capacity of 40 cu. in. [655ml], one (1) of the two (2) compartments shall have a minimum capacity of 14 cu. in. [229ml].

Body:  Manufacture box body from die-cast aluminum with stamped steel base.  Boxes shall be available in a two-gang configuration.  The box shall be supplied with a temporary construction cover; overall box dimensions are 8-1/4" [210mm] diameter x 6-1/2" [165mm] H.  Provide the box with the following trade size knockouts: three (2) 3/4-inch knockouts, one (1) 1-1/2-inch knockout, one (1) removable feed barrier 2" x 1-1/2" [51mm x 38mm].

Activation Covers:

Specifier Note:  Select one of the powder-coated finishes in the following two subparagraphs and delete the other finishes.  Delete the last sentence in the following subparagraph if a tamper-resistant cover assembly is not required.

6CTCFF Series Covers:  Manufacture from die-cast aluminum with [black powder coat] [gray powder coat] [brass powder coat] [nickel powder coat] [bronze powder coat] finish.  Provide cover assembly with gasketing to maintain scrub water tightness.  The cover shall be 7-3/4" [197mm] diameter.  Provide covers with one (1) 3/4" threaded conduit opening for power and One (1) 1-1/4 / 2" concentric threaded conduit opening for communications and audio/video services.  Each of the threaded openings is supplied with plugs installed.  The covers shall have separate access covers to allow for each of the services to be accessed individually.

Classification and Use:  Floor boxes shall have been examined and tested by Underwriters Laboratories Inc. to comply with UL514A and/or UL514C and Canadian Standard C22.2, No. 18-98 and bear the U.S. and Canadian UL Listing Mark.  Fire classified floor boxes shall also have been tested by UL and classified for fire resistance and bear the U.S. and Canadian UL Classification Mark.  The floor boxes shall conform to the standards set forth in the National Electrical Code, Section 300-21.

Floor boxes shall have been evaluated by UL to meet the applicable U.S. and Canadian safety standards for scrub water exclusion when used on tile, terrazzo, wood, and carpet covered floors.

These devices are not suitable for wet or damp locations, or other areas subject to saturation with water or other liquids such as commercial kitchens.

Floor boxes shall be suitable for use in air handling spaces in accordance with Section 300-22C of the National Electrical Code.

COMMUNICATION MODULES MOUNTING ACCESSORIES

The floor box manufacturer shall provide a complete line of faceplates and bezels to facilitate mounting of UTP, STP (150 ohm), fiber optic, coaxial, and communication devices. The box shall provide a series of device mounting plates that will accommodate Ortronics workstation connectivity outlets and modular inserts, Wiremold Connectivity Modular Insert System, and Extron® Electronics MAAP devices.

EXECUTION

EXAMINATION

Specifier Note:  Select either option in the following paragraph and delete the other one.

Examine conditions under which floor boxes, poke-thru devices, accessories, and fittings are to be installed.  Notify the [Architect/Engineer] [Construction Manager] in writing of conditions detrimental to proper completion of the work.  Do not proceed with work until unsatisfactory conditions have been corrected.

INSTALLATION

Strictly comply with manufacturer's installation instructions and recommendations and approved shop drawings.  Coordinate installation with adjacent work to ensure proper clearances and to prevent electrical hazards.

Mechanical Security:  Raceway systems shall be mechanically continuous and connected to all electrical outlets, boxes, device mounting brackets, and cabinets, in accordance with manufacturer’s installation sheets.

Electrical Security:  Metal raceway shall be electrically continuous and bonded in accordance with the National Electric Code for proper grounding.

Raceway Support:  Raceway shall be supported at intervals not exceeding 5 feet or in accordance with manufacturer’s installation sheets.

Accessories:  Provide accessories as required for a complete installation, including insulated bushings and inserts where required by manufacturer.

Unused Openings:  Close unused raceway openings using manufacturer's recommended accessories.

Install floor boxes to permit all wiring to be completed at floor level.

CLEANING AND PROTECTION

Clean exposed surfaces using non-abrasive materials and methods recommended by manufacturer.

Protect floor boxes until acceptance.

END OF SECTION

© 2013 Legrand/Wiremold.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Rev 07/13