Section 16110

Wallduct raceway specifications

PART 1 GENERAL

1.1	Scope

Work under this section includes all labor and materials, which are required for the completion of the Wallduct Raceway for electrical and communication services, as shown on drawings and as specified.

1.2	Classification and Use

This product series shall have been examined and tested by Underwriters Laboratories Inc. to Standard UL5 and Cul5 and bear the U.S. and Canadian UL Listing Mark.  This product series shall also conform to the standards set in the National Electric Code, Sections 300 and 660.

1.3	substitutions

No substitution will be considered unless written request for approval has been submitted by the bidder and has been received by the Architect at least ten days prior to the date for receipt of bids. Each such request shall include the name of the materials or equipment for which it is to be substituted and a complete description of the proposed substitute including drawings, cuts, mock-ups, performance and test data, compliance with codes and approvals, and any other information necessary for evaluation.

PART 2 PRODUCT

2.1	manufacturer

Wallduct with the accessories to provide a complete system furnished by Walker Systems, Inc., establish the minimum requirement for function, dimension, and appearance. The materials, products, and equipment specified in this section establish a standard of quality of required function, dimension, appearance, and quality to be met by any proposed substitutions. The manufacturer and installer shall certify that they have a minimum of five years’ experience with the type of raceway system specified in the section.

2.2	components

2.2.1	Wallduct Body Assembly

The wallduct raceway consists of a metal body and removable cover plates. The Wallduct Raceway shall be fabricated from 14 [2mm] gauge galvanealed steel. Standard body dimensions are 10" [254mm] wide x 3 1/2" [89mm] deep or 18" [475mm] wide x 3 1/2" [89mm] deep. Other width by depth configurations shall be made available as specified on the layout drawings. Cover plate widths shall be equal to the body width when raceway is surface mounted and shall exceed the body width by 1" [25mm] on each side when the raceway is flush mounted. The Wallduct Raceway shall be furnished in standard 5 ft. [1524mm] lengths unless otherwise specified. Each 5 ft. [1524mm] length shall consist of one body and two 30" [762mm] long cover plates. When necessary, the installer shall make modifications to the product to ensure compliance with the layout drawings.

2.2.2	Wallduct Accessories

The Wallduct Raceway shall be supplied with the necessary accessories as required to make a complete installation. Accessories shall include, but not limited to internal coupling angles, snap-in wire retainers, partitions, and end closures.

2.2.3	Wallduct Fittings

The manufacturer shall supply all tee, horizontal elbow and internal elbow fittings, as may be required. When necessary, fittings shall be supplied with tunneling to maintain separation of services. Transitions from Wallduct to Trenchduct Raceway shall also be supplied, as necessary. Other fittings may also be supplied to conform to the layout drawings.

PART 3 EXECUTION

3.1	Installation

Mounting shall be accomplished by means of screws or other acceptable fasteners to securely mount the system. Mounting devices shall be through the back or sides of the body. No exposed threads are permitted inside the raceway. The Wallduct and fittings are to be assembled using the coupling angles and screws provided. Install angles and screws on inside of body using pre-punched holes. Field cutting of straight lengths to fit project conditions is acceptable. Holes must be field drilled in body to match coupling angle holes with #20 drill (.161” dia.). Install screws provided from inside body. Maximum wire fill capacity shall not exceed 40% of the interior cross sectional area of the Wallduct.

# Text boxes

|  | Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2005 Legrand All Rights Reserved | ED934R3 – Updated January 2005 – For latest specs visit www.legrand.us |