SECTION 16130
Evolution™ Series poke-thru Devices

PART 1 GENERAL

1.1	Scope

These poke-thru devices provide the interface between power, communication and audio/ visual (A/V) cabling in an above grade concrete floor and the workstation or activation location where power communication and/or A/V device outlets are required. These poke-thru devices provide recessed device outlets that will not obstruct the floor area.

1.2	Classification and Use

This poke-thru device shall have been examined and tested by Underwriters Laboratories Inc. to Standard UL514A and/or UL514C and Canadian Standard C22.2, No. 18-98 and bear the U.S. and Canadian UL Listing Mark. This poke-thru device shall also have been tested by Underwriters Laboratories Inc. and classified for fire resistance and bear the U.S. and Canadian UL Classification Mark. Devices shall be classified for use in 1-, 1 1/2-, or 2-hour rated, unprotected reinforced concrete floors and 1-, 1 1/2-, or 2-hour rated floors employing unprotected steel floor units and concrete toppings (D900 Series Designs) or concrete floors with suspended ceilings (fire resistive designs with suspended ceilings should have provisions for accessibility in the ceiling below the poke-thru fittings. This device shall also conform to the standards set in the National Electric Code, Section 300-21. These devices meet all UL scrub water requirements, but are not suitable for wet or damp locations, or other areas subject to saturation with water or other liquids such as commercial kitchens. This poke-thru device shall also have been evaluated by UL to meet the applicable U.S. and Canadian safety standards for scrub water exclusion when used on tile, terrazzo, wood, and carpet covered floors. Suitable for use in air handling spaces in accordance with Sec 300-22 (C) of the National Electrical Code.

PART 2 PRODUCTS

2.1	Manufacturer

The Evolution Poke-Thru Devices described shall be manufactured by Wiremold/Legrand. The poke-thru device shall be compatible with the complete line of Ortronics® workstation connectivity outlets and modular inserts, or the Pass & Seymour Network Wiring System. Poke-thru devices of other manufacturers may be considered, if equal in functionality and quality, by written approval of the specifying engineer and shall meet all the performance standards specified herein. The same manufacturer shall provide all poke-thru types for the project. In addition, the contractor shall have ten days prior to the date for receipt of bids to submit to the specifying engineer a working sample from any other manufacturer.

  - materials

2.2.1	6AT Poke-Thru Assembly

This assembly consists of an insert and an activation cover. Overall poke-thru assembly length shall be 16 3/4" [425mm].

2.2.1.1 Insert:

The insert body shall recess the devices a minimum of 2 3/4” [69 mm] and have a polyester based backing enamel finished interior (ivory). There shall be the necessary channels to provide complete separation of power and communication services. There shall be three compartments that allow for up to three duplex receptacles that can be wired as a standard receptacle or isolated ground and/or twelve communication ports and/or ten of Extron® Electronics MAAP™ and/or two AAP™ devices.

The body will consist of an intumescent fire stop material to maintain the fire rating of the floor slab. The intumescent material will be held securely in place in the insert body and shall not have to be adjusted to maintain fire rating of the unit and the floor slab. The insert shall have retaining feature that will hold the poke-thru device in the floor slab without additional fasteners. The poke-thru insert shall also consist of a 3/4" trade size conduit stub that is connected to the insert body and a 24.5 cu. in. [402ml] stamped steel junction box for wire splices and connections. The stamped steel junction box shall also contain the necessary means to electrically ground the poke-thru device to the system ground.

2.2.1.2 Activation Cover:

The activation covers shall be manufactured of die-cast aluminum alloy and be available in powder-coated gray, black, or plated in brass, nickel or bronze finish. Two gaskets (one for carpet and one for tile) are provided to go under the trim flange to maintain scrub water tightness. The activation cover shall be 7 1/4" [184mm] in diameter. The activation covers shall be available in carpet and tile versions. The carpet covers shall be surface mounted and the tile covers shall be flush with the finished floor covering. The cover shall have spring loaded slides to allow cables to egress out of the unit and maintain as small an egress opening as possible.

2.2.1.3 Communication Modules Mounting Accessories:

The activation shall have three locations to mount communication connectors. Connectors shall be mounted using a mounting bracket. Mounting brackets shall be provided to mount up to twelve Ortronics TracJack Category 6 insert modules or TechChoice™ Category 6 discrete keystone connectors. The unit will also be supplied with two Category 6 keystone connectors and two Lucent® keystones. The unit shall also accommodate a mechanism to permit protection of communication cabling. This mechanism shall be stamped steel construction and accept both flexible and rigid conduit. This mechanism shall accept 3/4", 1-1/4" or 2" trade size conduits.

2.2.2	8AT Poke-Thru Assembly

This assembly consists of an insert and an activation cover. Overall poke-thru assembly length shall be 16 3/4" [425mm].

2.2.2.1 Insert:

The insert body shall recess the devices a minimum of 2 3/4" [69 mm] and have a polyester based backing enamel finished interior (ivory). There shall be the necessary channels to provide complete separation of power and communication services. There shall be five compartments that allow for up to five duplex receptacles that can be wired as a standard receptacle or isolated ground and/or twenty-two communication ports and/or sixteen of Extron® Electronics MAAP™ and/or four AAP™ devices.

The body will consist of an intumescent fire stop material to maintain the fire rating of the floor slab. The intumescent material will be held securely in place in the insert body and shall not have to 
be adjusted to maintain fire rating of the unit and the floor slab. The insert shall have retaining 
feature that will hold the poke-thru device in the floor slab without additional fasteners. The poke-thru insert shall also consist of a 3/4" trade size conduit stub that is connected to the insert body and a 24.5 cu. in. [402ml] stamped steel junction box for wire splices and connections. The stamped steel junction box shall also contain the necessary means to electrically ground the poke-thru device to the system ground.

2.2.2.2 Activation Cover:

The activation covers shall be manufactured of die-cast aluminum alloy and be available in powder-coated gray, black, or plated in brass, nickel or bronze finish. Two gaskets (one for carpet and one for tile) are provided to go under of the trim flange to maintain scrub water tightness. The activation cover shall be 9 1/4" [235mm] in diameter. The activation covers shall be available in carpet and tile versions. The carpet covers shall be surface mounted and the tile covers shall be flush with the

finished floor covering. The cover shall have spring loaded slides to allow cables to egress out of the unit and maintain as small an egress opening as possible.

2.2.2.3 Communication Modules Mounting Accessories:

The activation shall have three locations to mount communication connectors. Connectors shall be mounted using a mounting bracket. Mounting brackets shall be provided to mount up to twelve Ortronics TracJack Category 6 insert modules or TechChoice™ Category 6 discrete keystone connectors. The unit will also be supplied with two Category 6 keystone connectors and two Lucent® keystones. The unit shall also accommodate a mechanism to permit protection of communication cabling. This mechanism shall be stamped steel construction and accept both flexible and rigid conduit. This mechanism shall accept 3/4", 1-1/4" or 2" trade size conduits.

2.2.3	6AFF Poke-Thru Assembly

This assembly consists of an insert and an activation cover. Overall poke-thru assembly length shall be 16 3/4" [425mm].

2.2.3.1 Insert:

The insert body shall have the necessary channels to provide complete separation of power and communication services. There shall be two channels that allow for up to ten #10 AWG conductors in the power channel and twenty-eight category 6A data cables through the communication channel.

The body will consist of an intumescent fire stop material to maintain the fire rating of the floor slab. The intumescent material will be held securely in place in the insert body and shall not have to be adjusted to maintain fire rating of the unit and the floor slab. The insert shall have retaining feature that will hold the poke-thru device in the floor slab without additional fasteners. The poke-thru insert shall also consist of a 3/4" trade size conduit stub that is connected to the insert body and a 24.5 cu. in. [402ml] stamped steel junction box for wire splices and connections. The stamped steel junction box shall also contain the necessary means to electrically ground the poke-thru device to the system ground.

2.2.3.2 Activation Cover:

The activation covers shall be manufactured of die-cast aluminum alloy and be available in powder-coated gray, black, or plated in brass, nickel or bronze finish. Two gaskets (one for carpet and one for tile) are provided to go under the trim flange to maintain scrub water tightness. The activation cover shall be 7 3/4" [196mm] in diameter. The activation covers shall be available in the surface mount (carpet) version. The cover shall have one (1) 3/4" [19.05mm] trade size opening for power and one (1) 1 1/4" / 2" [31.75/50.8] combination trade size opening for communications.

PART 3 EXECUTIONS

3.1	Installation

Unit shall permit all wiring to be completed at floor level. The 6AT, and 6ATCFF units shall mount in a 6" [152mm] cored hole, actual 6 1/16" [154mm] core hole. The 8AT units shall mount in an 8" [203mm] cored hole, actual 8 1/16" [205mm] core hole. Use is defined by the UL Fire Resistance Directory as a minimum spacing of “2 ft. [610mm] on center and not more than one device per each 65 sq. ft. [6m2] of floor area in each span.”

Installation shall be completed by pushing unit down into the cored hole. Prior to and during installation, refer to system layout and/or approval drawings. Installer shall comply with detailed manufacturer’s instruction sheet included with each device. The unit shall contain a retainer for securing the device in the slab, as well as the necessary intumescent material to seal the cored hole under fire conditions.

Copper Cross Sectional Area

| Copper Cross Sectional Area of Commonly Used Conductors |
| --- |
| Size | Solid or Stranded |
| #24 | .00032 sq. in. [.206mm2] |
| #22 | .00050 sq. in. [.322mm2] |
| #14 | .00323 sq. in. [2.083mm2] |
| #12 | .00512 sq. in. [3.303mm2] |
| #10 | .00815 sq. in. [5.258mm2] |
| # 8 | .01296 sq. in. [8.361mm2] |

The maximum copper cross sectional area for the 6AT outer compartment only is 
.0154 sq. in. [9.9 mm2]. The maximum copper cross sectional area for the center compartment only is .0387 sq. in. [24.9mm2].

The maximum copper cross sectional area for the 6ATCFF power compartment only is 
.0815 sq. in. [52.6mm2]. The maximum copper cross sectional area for the center communi-
action compartment only is .0686 sq. in. [44.3mm2]. The maximum copper cross sectional area for the outside communication compartment only is .0187 sq. in. [12.1mm2].

The maximum copper cross sectional area for the 8AT outer compartment only is 
.0154 sq. in. [9.9 mm2]. The maximum copper cross sectional area for the center compartment only is .0775 sq. in. [16.6mm2].

.

# Text boxes

|  | Wiremold / Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 ( Outside U.S.: 860-233-6251 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2008 Wiremold/Legrand All Rights Reserved | ED1558 – February 2008 – For latest specs visit www.wiremold.com |