Eclipse™ latching surface nonmetallic raceway

PART 1 GENERAL

1.1	Scope

This specification covers a surface nonmetallic raceway system used for branch circuit wiring or data network, voice, video, and other low-voltage wiring. The nonmetallic raceway system shall consist of raceway, appropriate fittings, and device boxes to complete installation per electrical and datacom drawings.

1.2	Classification and Use

Surface nonmetallic raceway is to be utilized in dry interior locations only as covered in Article 388 of the National Electrical Code, as adopted by the National Fire Protection Association and as approved by the American National Standards Institute. The Wiremold Company's PN05L Raceway System is listed by Underwriters Laboratories for the U.S.A. and Canada, under File Nos. E90378 Guide RJTX and E90377 Guide RJYT.

PART 2 PRODUCT

2.1	Manufacturer

The surface nonmetallic raceway system specified herein for branch circuit wiring or data network, voice, video, and other low-voltage wiring shall be the PN05L System as manufactured by The Wiremold Company. Systems of other manufacturers may be considered equal if, in the opinion, and the written approval of the engineer, they meet all the performance standards specified herein.

2.2	Materials

The raceway and all system components must be UL Listed and exhibit nonflammable 
self-extinguishing characteristics, which comply with UL Standard UL5A.

The PN05L Series Raceway shall be manufactured of rigid PVC compound and flexible PVC for the hinge. The surface shall have a smooth texture and be available in ivory, white and fog white colors.

2.2.1	Raceway

The raceway shall be a one-piece design with a flexible hinge for access to the compartment. Total width shall be 1.13" [29mm] by 0.63" [16mm] deep with a cross-sectional area of 0.44" [11mm] square inches. The raceway shall have an approximate thickness of .051" [13mm]. The raceway base and cover shall be available in 8' [2.44m] and 10' [3.05m] lengths. The raceway shall have an adhesive tape backing.

A full compliment of fittings must be available including, but not limited to flat, internal, and external elbows, tees, cover clips, and end caps. The fittings shall have a matte texture, available in ivory, white and fog white to match the raceway. They shall overlap the cover and base to hide uneven cuts. All fittings shall be supplied with a base where applicable to eliminate mitering. A transition or reducer fitting shall be available to adapt to other raceways manufactured by The Wiremold Company.

2.2.2	Device and Fixture Boxes

Device boxes shall be available for mounting standard devices and faceplates. A device box shall be available in single- and two-gang configurations at a depth of 1.75" [44.5mm]. Device boxes shall be available in ivory, white and fog white to match the raceway.

2.2.3	Datacom Device Boxes

The raceway manufacturer will provide a complete line of datacom device boxes providing outward and downward facing connections to accommodate modular inserts for UTP, STP, fiber optic, coaxial, plus other cabling types with faceplates and bezels to facilitate mounting.

PART 3 EXECUTION

3.1	Installation

Prior to and during installation, refer to system layout drawing containing all elements of the system. Installer shall comply with detailed manufacturer's installation instruction sheets, which accompany system components, as well as complete system instruction sheets.

3.1.1	Raceway Support

Raceway shall be securely supported in accordance to manufacturer's installation instructions.

3.1.2	Completeness

Work shall include furnishing all raceway and appropriate fittings and device plates to install a complete nonmetallic surface raceway system as indicated on the electrical drawings and in this specification. All unused raceway openings shall be closed.

|  | Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2005 Legrand All Rights Reserved | ED1127R3 – Updated January 2005 – For latest specs visit www.legrand.us |