GUIDE SPECIFICATIONS

Wiremold®  4000 Series Raceway (Stainless Steel)

S4000 dual-channel stainless steel raceway

PART 1 GENERAL

1.1	Scope

This specification covers a surface metal raceway system used for branch circuit wiring and/or data network, voice, video and other low-voltage wiring. The metallic raceway system shall consist of raceway base, cover, appropriate fittings and device mounting plates to complete installation per electrical drawings.

1.2	Classification and Use

Surface metal raceway is to be utilized in dry interior locations only as covered in Article 386 of the National Electrical Code and in Sections 12-1600 to 12-1614 of the Canadian Electrical Code. The Wiremold Company S4000 Raceway System is listed by Underwriters Laboratories under File No. E4376 Guide RJBT for the raceway and File No. E41751 Guide RJPR for the fittings, all in accordance with publication UL5 for Surface Metal Raceways. The system is also certified by the Canadian Standards Association under File No. LR350 in accordance with publication C22.2 No. 62 for Surface Metal Raceways.

PART 2 PRODUCT

2.1	Manufacturer

The surface metal raceway system specified herein for branch circuit wiring and/or data network, voice, video and other low-voltage wiring shall be the S4000 System in accordance with the approval drawings as manufactured by Wiremold Canada Inc. Systems of other manufacturers may be considered equal if, in the opinion, and the written approval of the engineer, they meet all the performance standards specified herein.

2.2	Materials

The raceway and all system components must be UL Listed and CSA certified. Steel shall be stainless steel type 304 for all exposed surfaces. Finish shall be a #4 brush finish with a removable PVC coating for protection during shipping. Internal device brackets, couplings, wire clips, dividers and divider clips shall be galvanized steel.

2.2.1 Raceway

The raceway shall be a two piece design with a base and a snap-on cover. The base shall be a minimum of 0.048" [12.19mm] wall thickness and the cover shall be a minimum of 0.036" [.9144mm] wall thickness. Assembled base and cover shall be 4.750" [120.65mm] wide by 1.750" [44.45mm] high with a cross sectional area of 7.50 square inches [4838.7mm2]. The base shall be dividable by means of a removable barrier section into two equal compartments.

2.2.2 Fittings

A full line of fittings must be available including, but not limited to flat, internal and external elbows, couplings for joining raceway sections, wire clips, blank end fittings and a full compliment of device mounting brackets and plates.

2.2.3 Device Brackets and Plates

Device brackets and plates shall be available in 4.50" [114.3mm] lengths and 9.00" [228.6mm] lengths to accommodate mounting of various combinations of power and communication devices.

2.2.4 Communication Devices and Accessories

The raceway manufacturer will provide a complete line of connectivity outlets and modular inserts for UTP/STP, Fiber Optic, Coaxial and other cabling types with face plates and bezels to facilitate mounting.  A complete line of preprinted station and port identification labels, snap-in icon buttons as well as write-on station identification labels shall be available.

PART 3 EXECUTION

3.1	Installation

Prior to and during installation, refer to system layout drawings containing all elements of the system. Installer shall comply with detailed manufacturer’s instruction sheets which accompany system components, as well as complete system instruction sheets, whichever is applicable.

3.1.1 Mechanical Security

All raceway systems shall be mechanically continuous and connected to all electrical outlets, boxes, device mounting brackets and cabinets, also in accordance with manufacturer’s installation instruction sheets.

3.1.2 Electrical Security

All metal raceway shall be electrically continuous and bonded in accordance with the National Electrical Code and Canadian Electrical Code for proper grounding. Sharp edges shall be removed from field cut pieces to prevent damage to installed conductors.

3.1.3 Raceway Support

Raceway shall be securely supported at intervals not exceeding 10 feet [3.048m] or in accordance with manufacturer’s installation sheets.

3.1.4 Completeness

All raceway systems shall be installed complete, including insulating bushings and inserts where required by manufacturer’s installation sheets. Field cuts of raceway should be square such that no openings are present in the installed system. All unused raceway openings shall be closed.

|  | Legrand U.S. and International: 60 Woodlawn Street ( West Hartford, CT 06110 1-800-621-0049 ( FAX: 860-232-2062 Canada: 570 Applewood Crescent ( Vaughan, Ontario L4K 4B4 1-800-723-5175 ( FAX: 905-738-9721 |
| --- | --- |
| (2005 Legrand All Rights Reserved | ED591R2 – Updated January 2005 – For latest specs visit www.legrand.us |